- Approved by 
Order of the Federal Environmental, Industrial and Nuclear Supervision Service 
No. ___ dated ____________ 20__

SAFETY GUIDE 
IN THE USE OF ATOMIC ENERGY "ESTABLISHING AND METHODS OF MONITORING SERVICE LIFE CHARACTERISTICS OF VALVES FOR NUCLEAR POWER PLANTS"

(RB-131-17)

- I. General

1. The safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants" (RB-131-17) (hereinafter referred to as the Safety Guide) has been developed in accordance with article 6 of Federal Law No. 170-FZ dated November 21, 1995 "On the use of atomic energy" for facilitating compliance with the requirements of the following Federal Rules and Regulations for the use of atomic energy: "Rules for design and safe operation of equipment and piping of nuclear power installations" (NP-089-15) approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No. 521 dated December 17, 2015 (registered by the Ministry of Justice of the Russian Federation on February 9, 2106, registration No. 41010) (hereinafter No-089-15); "Requirements for life management of the equipment and piping of nuclear power plants. Principal provisions" (NP-096-15) approved by the Order of the Federal Environmental, Industrial and Nuclear Supervision Service No. 410 dated October 15, 2015 No. 410 (registered by the Ministry of Justice of the Russian Federation on November 11, 2015, registration No. 39666) (hereinafter referred to as NP-096-15).

2. This Safety Guide contains recommendations on the establishment and methods for monitoring the service life characteristics of nuclear power plant valves during their design and operation.

3. This Safety Guide applies to the casing and operating parts of shutoff, check, control and safety valves (safety devices) of nuclear power plants included in the service life management program according to the requirements of NP-096-15.

4. This Safety Guide is recommended for use by legal entities and individuals engaged in the design and operation of nuclear power plant valves.

5. This Safety Guide has been developed taking into account domestic and foreign experience in the service life management of valves for nuclear power plants.

6. The list of the abbreviations used in this Safety Guide is given in Appendix No. 1, and the terms and definitions are given in the Appendix No. 2.

7. The suggested list of NPP valves included in the life management program and falling under this Safety Guide is given in Annex No. 3. The operator may supplement the specified list by agreement with the developers of RP and NPP designs.

- II. Recommendations for establishing life characteristics

8. The life characteristics of NPP valves are recommended to be established and substantiated either by the engineering (design) company at the design stage, or by the operator if for any reason these characteristics were not stipulated at the engineering (design) stage.

9. The suggested list of parameters making the basis for determination of life characteristics of NPP valves is given in Appendix No. 4 to this Safety Guide. It is recommended to determine the life characteristics required for life management of the valves based on the parameters of the specified list, or (if the parameters given therein are not sufficient for determining the life characteristics), to additionally assign other parameters.

10. The life characteristics of NPP valves are determined as the maximum permissible values of the parameters given in Appendix No. 4, the attainment thereof corresponds to the exhaustion of life according to the life assessment criteria (refer to section IV of this Safety Guide).

11. The list of life characteristics of valves stipulated by the engineering (design) organization is recommended to be substantiated with the following to serve as substantiation:

references to the operation and life management experience of similar valves at nuclear power plants;

results of trial operation of the prototypes operated in the worst-case conditions for coolant parameters, actuation cycles, external and internal impacts;

predictive valve degradation mechanisms <2>.

--------------------------------

<1> For new developments.

12. In cases when the life characteristics of valves are stipulated by the operator, the list of life characteristics is recommended to be agreed upon with the organization that performed design engineering (designing) of the specified valves (excluding the cases when the design organizations ceased to exist or are foreign legal entities).

- III. Recommendations for the establishment of life assessment criteria

13. The valve life assessment criteria are recommended to be stipulated for each life characteristics from those intended for the valve in question based on:

the requirements of the Federal Rules and Regulations in the field of atomic energy use;

requirements of national standards included in the consolidated list of documents on standardization in the field of atomic energy use, applied on a mandatory basis;

requirements of engineering (design) documentation.

14. A suggested list of criteria for assessment of the NPP valve life is given in Appendix 5 hereto. It is recommended to determine the life assessment criteria necessary for managing the life of valves using the specified list. If it is necessary to use other criteria for life assessment that are not specified in Appendix 5 hereto or additional sources for the determination of numerical values of life criteria, the design organization shall be encouraged to substantiate the need to use alternative criteria.

- IV. Recommendations for monitoring methods of the life characteristics of valves

15. The life characteristics of NPP valves are recommended to monitor for all the valves included in the life management program, whose service life is to be managed according to NP-096-15, for the purpose of periodic or continuous (using automated systems to monitor residual life) assessment of technical condition and identification of the dominant (determining) mechanisms of aging, degradation and damages of these valves.

16. The valve engineering design organization (designer) is recommended to the give the life characteristics and monitoring methods of the life characteristics in the operation manual specifying the periodicity of replacement of the in-vessel components of the valve with an entry made in the list of replaced components in the valve datasheet.

17. The life characteristics of the NPP valves at the operation stage are monitored in accordance with the equipment and piping life management Program, which is developed by the operator for each NPP power unit and agreed with the developers of RP and NPP designs.

18. The life of valves is confirmed, maintained and, if technically possible, restored by M&R with periodicity determined in the equipment and piping life management Program.

19. In the cases when the residual life of a valve has ended, the valve shall be replaced. On valve replacement the relevant changes including the required life characteristics monitoring actions for the newly installed valve are entered in the Life Management Program of equipment and piping.

20. The operator is recommended to determine the list of non-replaceable valves, the life of which must be provided before the decommissioning of the power unit, as well as the valves engaged during decommissioning of the NPP, the life of which must be ensured for the decommissioning period, as well.

21. The required condition for performing life characteristics monitoring procedures subject to life management of NPP valves is the monitoring of the actual operation conditions of these valves, for which purpose it is recommended to monitor (by direct measurements or using indirect calculation assessment) the following parameters:

operating time;

housing wall temperature;

temperature of coolant or other fluid;

warmup or cooldown rate;

temperature gradients across the housing wall thickness;

pressure and rate of increase or drop of pressure of coolant or working media;

vibration characteristics (within the system in which the valves are installed);

coolant or working media flow rate;

number of cycles of loading with internal pressure;

number of actuations;

opening/closing time;

pressure of hydraulic (pneumatic) tests (including as part of the circuit in which the valve is installed) for strength and tightness.

22. In addition to the parameters given in paragraph 21 it is recommended to record and account the operation time of valves in every mode, and accounting for the actual number of implementations of a particular mode of operation, including hydraulic (pneumatic) tests of valves for strength and tightness.

23. The parameters given in the paragraph 21 hereto are recommended to be monitored either by direct methods (regular or periodic measurement in the operation process), or by indirect methods (through recalculation, extrapolation or interpolation).

24. If it is impossible to directly or indirectly monitor the parameters given in paragraph 21 hereto, it is recommended to stipulate the procedure for retrofitting the valves of the NPP with the systems and/or methods to monitor necessary parameters from the above list.

25. The recommended methods for valve life characteristics monitoring using the parameters given in paragraph 21 hereto are specified in Appendix No. 6.

- V. Recommendations for the collection, systematization and storage of data on valves of nuclear power plants

26. For NPPs under construction and design, it is recommended that the operator organizes and adjusts the system of collection, processing, systematization, analysis and storage of information on damage of valves, their accumulation and development, ageing mechanisms, failures and malfunctioning, as well as on operation modes, including transient modes, hydraulic (pneumatic) tests and emergency situations before commissioning an NPP power unit.

27. The specified information is recommended to be kept throughout the lifetime of the valve as a computer database allowing to immediately obtain all the required parameters for assessment of the residual life of the valve, if required.

28. The following data shall be entered into the database specified in paragraph 26 of this Safety Guide for each unit of NPP valves whose service life is subject to management:

all nominal data for the valves in compliance with the requirements of NP-068-05 and NP-089-15;

data from manufacturers of electrical equipment of NPP and installation organizations on the presence or absence of deviations from the engineering (design) documentation for valves of the NPP and on its manufacture technology, repairs, heat treatment procedures, additional tests;

information about the presence or absence of deviations from the engineering (design) documentation for NPP equipment during their storage, shipment and handling operations;

technical characteristics of existing deviations (if any) during manufacturing, storage, transportation and installation of valves;

data on the monitoring of actual operation conditions of valves given in paragraph 21 hereof;

full information on the results of the conducted metal inspection;

data on damage of valves (or metal of valves), their accumulation and development, ageing mechanisms, failures and malfunctioning.

29. It is recommended to develop mathematical tool and software of the database so as to compare the initial and actual values of life characteristics of valves at any stage of the life cycle of an NPP power unit, and to analyze information about the operating conditions of NPP valves and impact of these conditions on the life.

30. DB is recommended to store using current data storage devices with mandatory duplication of information as backup copies allowing restoration of the full scope of information if lost or damaged. It is recommended to use information storage media not linked to public access networks during storage of DB copies.

31. It is recommended for the operator to make a scheduled plan for development and commissioning of a computer database for the NPP in the operation stage.

- Appendix No. 1 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

ABBREVIATIONS

The following abbreviations are used in this Safety Guide:

| NPP | - | Nuclear Power Plant |
| --- | --- | --- |
| NPF | - | Nuclear Power Facility |
| FSIV | - | fast-acting steam isolation valve |
| FNR | - | Sodium Cooled Fast Neutron Reactor |
| BRU-A | - | steam dump valve to atmosphere |
| VVER | - | pressurized water reactor |
| - | - | reactor coolant pipeline |
| PORV | - | pilot-operated relief valve |
| RFCC | - | Repeated Forced Circulation (Coolant) Circuit |
| SG | - | Steam Generators |
| RBMK | - | High Power Channel Type Reactor |
| RC | - | reactor compartment |
| RLAMS | - | Residual lifetime automated monitoring system |
| ECCS | - | emergency core cooling system |
| M&R | - | maintenance and repair |
| EGP-6 | - | Heterogeneous Loop Type Power Reactor with 6 Coolant Circulation Loops |

- Appendix No. 2 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

TERMS AND DEFINITIONS

The following terms and definitions are used for the purposes of this Safety Guide <1>.

--------------------------------

<1> Only terms are provided here that are not included in NP-096-15 "Requirements for service life management of equipment and pipelines of nuclear power plants.  Main provisions" and GOST 24856-2014 "Pipeline valves. Terms and definitions".

1. The dominant mechanism of ageing, degradation, damage of valves is one of several mechanisms of ageing, degradation, and damage to valves that leads to their fastest life depletion.

2. Leakage (internal) - the amount of the working medium leaking during operation through the closed gate of shutoff or safety valves.

3. Leakage (external) - the amount of working medium that flows out during operation through seals, gaskets and glands.

- Appendix No. 3 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

SUGGESTED LIST OF 
VALVES OF NPP INCLUDED IN THE LIFE MANAGEMENT PROGRAM

1. Valves of NPP with VVER reactors included in the life management program:

main isolation gate on the MCP;

PORV of pressurizer system;

shutoff valve DN100 of pressurizer system;

check valve DN100 of pressurizer system;

control valve DN100 of pressurizer system;

fast-acting isolating valve DN125 of pressurizer system;

isolating valve DN125 of pressurizer system;

shutoff valve DN50 of pressurizer system <1>;

--------------------------------

<1> The specified valves are included in the service life management program if It is impossible to replace them during the design life of the NPP.

shutoff valve DN32 of pressurizer system <1>;

shutoff valve DN15 of pressurizer system <1>;

control valve DN50 of pressurizer system <1>;

pilot-operated relief valve of ECCS;

fast-acting isolating valve DN300 of ECCS;

check valve DN300 of ECCS;

shutoff valve DN15 of ECCS <1>;

bellows shutoff valve DN15 of emergency gas removal system <1>;

bellows shutoff valve DN32 of emergency gas removal system <1>;

bellows shutoff valve DN65 of emergency gas removal system;

BRU-A;

SG PORV;

FSIV;

valves on pipelines of secondary circuit and feed water from the feeding assembly to the SG;

reactor compartment controllers.

2. Valves of NPP with RBMK reactors included in the life management program: valves DN800 of RFCC.

3. Valves of NPP with fast neutron reactors included in the life management program: shut-off valves for sodium-containing systems and safety systems.

4. Valves of NPP with EGP-6 reactors included in the life management program:

shut-off valves DN10, 20, 32, 36, 65, 100 of feed water, fresh steam, main circulation circuit systems, reactor control and protection systems;

main steam valve;

stop valve of turbine unit;

pilot-operated relief valve of main safety valve;

feed water control valve DN100;

feed water check valve DN65;

fresh steam shutoff valve DN200.

- Appendix No. 4 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

SUGGESTED LIST 
OF PARAMETERS BASED THEREOF THE LIFE CHARACTERISTICS OF NPP VALVES MAY BE DETERMINED

1. Operating time (for control valves and valves operated under creep conditions).

2. Total wall thickness of the housing and other valve components.

3. In-situ wall thickness of the housing or other valve components.

4. The value of accumulated fatigue damage to metal (including welds) of the housing or other valve components under cyclically repeated loads.

5. Offset of ductile to brittle transition temperature of metal of welded joints and basic metal of valve housing following temperature ageing and cyclic metal fatigue <1>.

--------------------------------

<1> The specified parameter is used only in the cases when the calculation of valve housing for brittle fracture resistance is mandatory.

6. Accumulated value of plastic deformations of the housing or other valve components.

7. Accumulated value of creep deformations of the housing or other valve components.

8. changes in the size and shape of the housing or other valve components due to elastic and non-elastic deformations.

9. Mechanical characteristics of structural materials of non-replaceable valve components.

10. Quality change of valve component metal structure leading to appearance of new mechanisms of its degradation and accelerated end of life.

11. Maximum value of external leakage established in the design engineering documentation.

12. Maximum internal leakage value (for shutoff or safety valves).

13. Irreversible changes of the valve process parameters due to depositions, corrosion, wear or chafing, change of valve geometric dimensions or shape.

14. Number of safety valve actuation cycles.

- Appendix No. 5 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

SUGGESTED LIST OF 
NPP VALVE LIFE ASSESSMENT CRITERIA

| No. | Parameter | Life assessment criterion (criteria) | Note |
| --- | --- | --- | --- |
| 1. | Operating time | Limit value set in the engineering documentation | It is recommended to enter this value in the data sheet and maintain records with entering of information in the data sheet. |
| 2. | Total wall thickness of the housing and other valve components. | Minimum value for which the requirements of calculation for section of the basic dimensions regulated by the Federal Rules and Regulations for atomic energy use stipulating the norms of strength calculation of nuclear power generating facility equipment and piping <1> | It is recommended to enter in the datasheet and maintain control with entering of information in the datasheet (following control in accordance with the Life Management Program) |
| 3. | In-situ wall thickness of the housing or other valve components. | Minimum value for which the strength conditions are met during verification analysis for mechanical strength given in the Federal Rules and Regulations for atomic energy use establishing the norms of strength calculation of nuclear power generating facility equipment and piping <1> | It is recommended to enter in the datasheet and maintain control with entering of information in the datasheet (following control in accordance with the Life Management Program) |
| 4. | The value of accumulated fatigue damage to metal (including welds) of the housing or other valve components under cyclically repeated loads. | Limit value given in the Federal Rules and Regulations in the field of atomic energy use establishing the norms of strength calculation of nuclear power generating facility equipment and piping <1> |  |
| 5. | Offset of ductile to brittle transition temperature of metal of welded joints and basic metal of valve housing and other valve components following temperature ageing and cyclic metal fatigue <2> | Limit value for which the strength conditions during brittle fracture resistance calculation given in the Federal Rules and Regulations for atomic energy use establishing the norms of strength calculation of nuclear power generating facility equipment and piping <1> |  |
| 6. | Accumulated value of plastic deformations of the housing or other valve components | Limit value of structural material |  |
| 7. | Accumulated value of creep deformations of the housing or other valve components. | Limit value of structural material |  |
| 8. | Changes in the size and shape of the housing or other valve components due to elastic and non-elastic deformations | Stipulated in the engineering (design) documentation |  |
| 9. | Mechanical characteristics of structural materials of non-replaceable valve components | Limit values for structural materials |  |
| 10. | Quality change of valve component metal structure leading to appearance of new mechanisms of its degradation and accelerated end of life | Set by the operator following in-service inspection of metal by agreement with the engineering organization (if any) and specialized material organization | It is recommended to enter in the data sheet (following monitoring in accordance with the Life Management Program) |
| 11. | Maximum value of external leakage established in the design engineering documentation | Set in the operation manual |  |
| 12. | Maximum internal leakage value (for shutoff or safety valves) | Set in the operation manual |  |
| 13. | Irreversible changes of the valve process parameters due to depositions, wear or chafing, change of geometric dimensions or shape | Set in the operation manual |  |
| 14. | Number of safety valve actuation cycles | Set in engineering documentation | Recommended to be entered in the datasheet after each actuation |
| 15. | State of replaced components | Limit value set in the design engineering documentation | It is recommended to be entered in the datasheet (the list of replaced components, periodicity of in-vessel components in the data sheet) and keep records. |

--------------------------------

<1> For the components not falling under the Federal Rules and Regulations for atomic energy use, the strength calculation is made in accordance with the current state of art.

<2> only for components that require a brittle fracture resistance calculation.

- Appendix No. 6 to the 
safety guide in the use of atomic energy "Establishing and methods of monitoring service life characteristics of valves for nuclear power plants", approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No.  _____ 
dated ____ __________ 20__

RECOMMENDED METHODS FOR 
MONITORING OF VALVE SERVICE LIFE CHARACTERISTICS

| No. | Life characteristic | Recommended monitoring methods |
| --- | --- | --- |
| 1. | Operating time | Any method registering the time of operation with an accuracy within one hour |
| 2. | Total wall thickness of the housing and other valve components. | Ultrasonic wall thickness test; visual and measuring control |
| 3. | In-situ wall thickness of the housing or other valve components. | Ultrasonic wall thickness test; visual and measuring control |
| 4. | The value of accumulated fatigue damage to metal (including welds) of the housing or other valve components under cyclically repeated loads. | Calculated estimates, automatic method (when using RLAMS), or experimental methods |
| 5. | Offset of ductile to brittle transition temperature of metal of welded joints and basic metal of valve housing and other valve components following temperature ageing and cyclic metal fatigue <1> | Calculated estimates or experimental methods (based on results of tests) |
| 6. | Accumulated value of plastic deformations of the housing or other valve components | Calculated estimates or experimental methods (based on results of measurements) |
| 7. | Accumulated value of creep deformations of the housing or other valve components. | Calculated estimates or experimental methods (based on results of measurements) |
| 8. | Changes in the size and shape of the housing or other valve components due to elastic and non-elastic deformations | Calculated estimates or experimental methods (based on results of measurements) |
| 9. | Mechanical characteristics of structural materials of non-replaceable valve components | Experimental methods (following direct or indirect measurements, tests) and/or using studies on samples |
| 10. | Quality changes of metal structure leading to appearance of new mechanisms of its degradation and accelerated end of life | Experimental methods, studies of metal samples |
| 11. | Maximum value of external leakage established in the design engineering documentation | Direct or indirect measurement methods in the course of operation or during inspections |
| 12. | Maximum internal leakage value (for shutoff or safety valves) | Direct or indirect methods of measurement in the process of operation, inspection or control |
| 13. | Irreversible changes of the valve process parameters due to depositions, corrosion, wear or chafing, change of valve geometric dimensions or shape | Calculated estimates or experimental methods |
| 14. | Number of actuation cycles (for safety valves) | Accounting of actual cases of actuation |
| 15. | Reliability targets | Tests and (or) analysis of operation results |

--------------------------------

<1> only for components that require a brittle fracture resistance calculation.

Note. For control and monitoring of service life characteristics, it is recommended to apply the methods, which are included in the norms and rules in atomic energy use, national standards (preliminary national standards), safety guidelines or metal control procedures.