- Approved by 
 Order of the Federal Environmental, Industrial and Nuclear Supervision Service No. ___ 
dated _______________, 20__

SAFETY GUIDE 
IN THE USE OF ATOMIC ENERGY "ESTABLISHMENT AND MONITORING METHODS OF THE LIFE CHARACTERISTICS OF INSTRUMENTATION AND CONTROL DEVICES OF NUCLEAR POWER PLANTS"

(RB-138-17)

- I. General

1. The safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" (RB-138-17) (hereinafter referred to as the Safety Guide) has been developed in accordance with the article 6 of the Federal law No. 170-FZ dated November 21, 1995 No. 170-ФЗ "On atomic energy use" to promote the compliance with requirements of federal rules and regulations in the field of atomic energy use "Basic requirements for life extension of NPP power unit" (NP-017-2000), approved by the Resolution of Gosatomnadzor of Russia dated September 18, 2000 No. 4, "Requirements for life management of equipment and pipelines of nuclear power plants. Main provisions" (NP-096-15) approved by Order of the Federal Environmental, Industrial and Nuclear Supervision Service No. 410 dated October 15, 2015 No. 410 (registered by the Ministry of Justice of the Russian Federation on November 11, 2015, registration No. 39666) (hereinafter referred to as NP-096-15).

2. This Safety Guide contains recommendations of the Federal Environmental, Industrial and Nuclear Supervision Service on the establishment and monitoring methods of the life of instrumentation and control devices of nuclear power plants during their design, engineering, manufacturing, operation and decommissioning.

3. This Safety Guide applies to instrumentation and control devices of nuclear power plants that are included in the life management program according to NP-096-15.

4. This Safety Guide is recommended for use by legal entities and individuals (officials) engaged in the design, engineering, manufacturing, operation and decommissioning of instrumentation and control devices of nuclear power plants.

5. The provisions of this Safety Guide should be taken into account when developing requirements of the operating organization for the purchased instrumentation and control devices of nuclear power plants.

6. This Safety Guide has been developed with regard to domestic and foreign experience in the life management of instrumentation and control devices of the nuclear power plants.

7. The list of abbreviations used in this Safety Guide is given in Appendix 1. Terms and definitions are given in Appendix 2.

- II. A list of instrumentation and control devices of nuclear power plants

8. A suggested list of I&C of nuclear power plants included in the life management program is given in Appendix 3 to this Safety Guide.

9. The operating organization in consultation with the developers of RP and NPP designs shall supplement the list with certain types of I&C assigned to safety classes 2 or 3 in the design of NPP power unit based on operating experience, experience of life management of I&C, and based on the possibility to replace I&C when their life is over.

10. When the specified list is supplemented with certain types of I&C, the NPP design shall provide a justification for assigning the I&C to the list.

- III. Recommendations for establishing life characteristics

11. It is recommended to provide established and justified life characteristics and service life for all I&C included in the life management program in the design of NPP and in the design and operational documentation. Design organization shall establish  and justify life characteristics and service life of NPP I&C at the design stage.

12. It is recommended to specify the service life and life characteristics in the data sheets of I&C. The operating organization shall be encouraged to issue data sheets for I&C that do not have ones.

13. As to I&C whose life characteristics were not established at the design stage, the operating organization shall be encouraged to develop a method to manage the life of this I&C and establish life characteristics. When developing the method, it is recommended to take into account the basic principles of life management in terms of predicting the mechanisms of damage to I&C, monitoring of life characteristics and identification of the dominant mechanisms of aging and degradation at the operation stage, and periodic assessment of the actual condition of I&C and their residual life.

14. A suggested list of parameters that determine the life of I&C, for which the life characteristics are set, is given in Appendix 4 to this Safety Guide. The life characteristics necessary to manage the life of I&C shall be set with regard to the specified list of parameters or, if the parameters specified are not sufficient to manage the life, other parameters shall be assigned additionally. When assigning new life characteristics to equipment that is already in operation, it is recommended to provide a justification for the choice of parameters that determine the life of I&C in the NPP design.

15. The list of parameters that determine I&C life established by the engineering (design) or operating organization shall be justified with due regard to:

experience in the design, manufacturing, installation, commissioning, operation and decommissioning of I&C;

results of trial operation of prototypes;

results of analytical studies;

results of specimen test, including accelerated aging test results;

anticipated I&C aging and degradation mechanisms.

16. When the life characteristics of I&C are set by the operating organization, it is recommended to coordinate the selection of parameters that determine the life of equipment for which the life characteristics are set with the organization that performed the design of the specified I&C, except for cases when the design organizations no longer operate or are located outside the Russian Federation.

- IV. Recommendations for the establishment of assessment criteria for instrumentation and control devices life

17. For all groups of I&C in the NPP design, it is recommended to provide established and justified limit values of life characteristics in order to determine the criteria for life assessment.

18. It is recommended that the design organization should set the limit values of life characteristics of I&C at the design stage for each life characteristic established for this device in accordance with:

requirements of federal rules and regulations in the field of atomic energy use;

requirements of national standards included in the consolidated list of mandatory standardization documents in the field of atomic energy use;

requirements of design documentation.

19. A suggested list of criteria for the evaluation of parameters that determine the life of NPP I&C is given in Appendix 5 to this Safety Guide. It is recommended to determine the life assessment criteria necessary for managing the life of I&C using the specified list. If it is necessary to use other criteria for life assessment that are not specified in Appendix 5 to this Safety Guide or additional sources for the determination of numerical values of life criteria, the design organization shall be encouraged to justify the need to use alternative criteria in the NPP design.

20. When assessment criteria of I&C life are established by the operating organization, they shall be coordinated with the organization performing the design and manufacturing of the specified I&C, except when the design organizations no longer operate or are located outside the Russian Federation.

- V. Recommendations for monitoring methods of the life characteristics of I&C

21. Monitoring of life characteristics of I&C of a NPP power unit shall be performed for all types of I&C included in the program of life management, whose life is to be managed according to NP-096-15, for the purpose of periodic or continuous (using automated systems to monitor parameters of technical state) assessment of technical state and identification of the dominant (determining) mechanisms of aging and degradation of this I&C.

22. When developing a life management program that provides methods for monitoring life characteristics, it is recommended to take into account the requirements of GOST R IEC 61513-2011 (in terms of requirements for functional and operational characteristics of safety-related control and monitoring systems), GOST R IEC 62342-2016 (in terms of aging management of systems and elements important for safety), GOST R IEC 62385-2012 (in terms of methods to assess the performance of measuring channels of safety systems, including methods for mutual calibration and measurement of response time of measuring channels).

To implement the requirements of NP-096-15 to the content of the life management program, it is recommended to provide the following as part of the program for a specific NPP power unit:

1) to form (taking into account the features of processes and mechanisms of degradation) major standard groups of I&C and establish a list of I&C of the power unit, which require life management;

2) to determine and set the scope of monitoring of the technical state of I&C of the power unit;

3) to set criteria of I&C limiting states;

4) to determine methods for detecting damages, including typical damages to I&C;

5) to determine the frequency and scope of monitoring the technical state of I&C.

It is recommended to set the following periods for the inspection of technical state:

operational monitoring during the current operation;

monitoring and instrumental diagnostics during SPM (performed every 18 months);

monitoring and technical diagnostics, analytical and computational methods, accelerated aging test methods during periodical safety assessment of a nuclear installation (every 10 years) before the expiration of the specified operating life;

monitoring and instrumental diagnostics, analytical and computational methods, accelerated aging test methods during the extension of operating life;

6) to define methods for predicting the residual lifetime based on standardized calculation norms, including:

predicting residual life of I&C components;

estimation of the residual lifetime based on changes in the controlled parameters;

7) to determine methods for improving the information content of I&C technical state monitoring, including:

assessment of technical state using statistical methods;

planning the minimum required scope of monitoring and technical diagnostics;

reducing the scope of monitoring by using the distribution of extreme values.

23. The operating organization shall be encouraged to arrange the monitoring of life characteristics of I&C with the involvement of specialized organizations that have the necessary licenses and qualified experts with relevant experience.

24. Monitoring of I&C life characteristics includes the following stages:

checking the availability of technical documentation;

checking compliance with operating conditions, including with regard to actual characteristics recorded in the forms;

performing operational reliability analysis;

checking compliance with the maintenance and repair regulations;

testing and measurements of life characteristics during operation;

comparison of life characteristics assessment results with assessment criteria of life and limiting states;

documenting based on the results of monitoring.

25. It is recommended to carry out monitoring of life characteristics based on the following diagnostic information:

data sheet information for I&C;

data on the technical state of I&C at the beginning of operation;

data on the current technical state based on results of measurements and examinations;

results of calculations, assessments, preliminary forecasts and conclusions;

summary data for I&C that is not specified above.

26. Prior to the monitoring of I&C life characteristics to be managed, it is recommended to monitor the actual operating conditions of this I&C. For this purpose, the following parameters shall be monitored at the NPP:

temperature, pressure, humidity in the locations of I&C;

radiation exposure levels;

vibration characteristics;

the intensity of electromagnetic field in the locations of I&C;

characteristics of external impacts;

output signals of electronic units;

results of preventive tests;

faults, their nature and methods of elimination;

amount and values of systematic and emergency overloads;

number of switch-ons and switch-offs.

27. In addition to the parameters given in paragraph 26 of this Safety Guide, it is recommended to register and record the storage time (inter alia, comply with the manufacturer's conditions for preservation and re-preservation, methods of protection against corrosion during operation and scheduled preventive repairs) and the time of actual operation of I&C.

28. Parameters specified in paragraph 26 of this Safety Guide shall be monitored with continuous or periodic measurements during operation in accordance with the life management program, with regard to requirements of paragraph 22 of this Safety Guide.

29. Where it is impossible to measure the parameters specified in paragraph 26 of this Safety Guide, the operating organization shall establish during operation the procedure for upgrading NPP I&C  with instrumentation diagnostics systems and/or controls of required parameters from the list given in paragraph 26 of this Safety Guide.

30. Recommended methods for the monitoring of life characteristics of I&C are given in Appendix 6 to this Safety Guide. Appendix 7 to this Safety Guide contains a list of regulatory documents recommended for use during the monitoring of life characteristics.

31. It is recommended to develop a procedure for the monitoring of life characteristics with a description of necessary means for monitoring and measuring life characteristics for the implementation of the methods given in Appendix 6 to this Safety Guide. The applied procedures for the monitoring of life characteristics shall be qualified by the operating organization in accordance with the established procedure, and measuring tool shall be registered in the register of measuring tools.

32. It is recommended to monitor life characteristics based on a conservative approach, with regard to the uncertainties of determination of each life characteristic. The procedure developer shall provide a method to assess the uncertainty of a life characteristic, with regard to the results of measurements and tests carried out during monitoring.

33. The results of monitoring shall be documented and results of tests and measurements (including certificates and reports with measurement results) shall be recorded to define residual life and predict future degradation.

34. Based on the results of monitoring, the operating organization shall decide on the possibility and conditions for further operation of I&C, including the development of measures to mitigate aging mechanisms.

- VI. Recommendations for the collection, systematization and storage of data on I&C of nuclear power plants

35. For NPPs under construction and design, it is recommended that the operating organization should organize and adjust the system of collection, processing, systematization, analysis and storage of information on damages, their accumulation and progress, failures and malfunctioning, as well as on operation modes, including tests, as well as pre-emergency situations and accidents prior to the commissioning of a NPP power unit.

36. It is recommended to keep the information specified in paragraph 35 of this Safety Guide throughout the service life of I&C in the form of a computer database that allows, if necessary, to quickly compare the design and actual life characteristics of I&C at any stage of the life cycle.

37. It is recommended to make up an operational file of a product in the database mentioned in paragraph 36 of this Safety Guide, for each I&C device with its life to be managed. The following data shall be included in the file:

all data sheet information for electrical equipment;

data from manufacturers of I&C of NPP power unit and installation organizations on the presence or absence of deviations from the design documentation and data on the technology of its manufacture, repair and additional tests;

data on specialized organizations that provide services to the operating organization for operation support and diagnostics of I&C;

information about the presence or absence of deviations from the design documentation for NPP equipment during their storage, shipment and handling operations;

technical characteristics of existing deviations (if any) during manufacturing, storage, transportation and installation;

test parameters of I&C during commissioning of NPP;

information about I&C operation experience;

data on the monitoring of actual operation conditions of I&C listed in paragraph 26 of this Safety Guide;

data on damages, their accumulation and progress, aging mechanisms, failures and malfunctioning;

results of life characteristics monitoring and their comparison with life assessment criteria;

data on the assessment of residual life of I&C operated during the extended service life.

38. The operating documentation for I&C shall establish the procedure for the collection and systematization of data on NPP I&C for information support of the database. Life management program shall justify possibility and the procedure for the recovery of missing data, if it is absent.

39. It is recommended to develop mathematical support and software of the database so as to compare the initial and actual values of life characteristics of I&C at any stage of the life cycle of an NPP power unit, and to analyze information about the operating conditions of I&C and their impact on the lifetime.

40. The procedure for forming and keeping the database updated shall be determined by the instructions for database maintenance and depend on the choice of database management system. It is allowed to use automated database management systems using proven and publicly available software.

41. It is recommended to store the database both in electronic and print format. Access to the database shall be limited to the number of officials responsible for the monitoring of life characteristics. It is recommended to control access to the database by the identification of users and registration of events.

42. To restore the data included in the database, it is recommended to provide for a backup copy on a separate accounted media in case of logical or physical failures.

43. For NPPs at the stage of operation where database maintenance is not provided, the operating organization shall be encouraged to arrange the development and installation of the database specified in paragraph 36 of this Safety Guide.

- Appendix 1 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

ABBREVIATIONS

| EP | - | Emergency Protection |
| --- | --- | --- |
| NPP | - | nuclear power plant |
| IR | - | Infrared |
| I&C | - | Instrumentation and Control Devices |
| PP | - | Preventive Protection |
| SPM | - | Scheduled Preventive Maintenance |
| RF | - | Reactor Facility |
| ULCS | - | Unit Level Control System |
| PHRS | - | passive heat removal system |
| CPS | - | Control and Protection System |
| M | - | Maintenance |
| ESFAS | - | Engineered Safety Features Actuation System |

- Appendix 2 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order 
No. _______ dated ____ __________ 20__

TERMS AND DEFINITIONS

The following terms and definitions are used for the purposes of this Safety Guide <1>.

--------------------------------

<1> Only terms and definitions that are not included in NP-096-15 are given.

1. The dominant mechanism of ageing, degradation, and damage of I&C is one of several mechanisms of ageing, degradation, and damages of I&C that leads to the fastest life depletion.

2. Life cycle [of a product] is a set of stages of successive changes in the state of the product during its existence.

3. Extended service life refers to the calendar duration (period) of a NPP unit power operation beyond the specified service life (NP-017-2000).

4. Tests are experimental assessment of qualitative and/or quantitative features and properties of a test item as a result of impact on the latter during its operation, during simulation of the item and/or impacts (GOST 16504-81). The definition includes evaluation and/or monitoring.

5. Control cable is a cable for remote control, relay protection and automatic equipment (GOST 15845-80).

6. Instrumentation cable is a cable for monitoring circuits and remote measurement of electrical and physical parameters (GOST 15845-80).

7. Limiting state criterion is a sign or set of signs of the limit state of an object (equipment, product, element) established by its documentation (reference and/or design) (GOST 27.002-2015). Depending on the operating conditions, two or more limit state criteria can be set for the same object.

8. Instrumentation and control devices (I&C) iss a set of instrumentation and actuators designed to perform information and control functions of process protection.

9. Technical state monitoring is an integral part of maintenance, which involves observation of the object in order to obtain information about its technical state and operating parameters (GOST 27.002-15). Monitoring can be carried out continuously or at scheduled intervals during the object operation. Monitoring data are used to monitor the technical state and residual life of the object.

10. Down state refers to the state of an object when it is not able to perform at least one required function for reasons that depend on it, or because of preventive maintenance (GOST 27.002-15).

11. Test specimen is a product or its part or a sample that is directly subjected to the experiment during testing (GOST 16504-81).

12. Failure refers to an event involving impaired up state of an object (GOST 27.002-2015). A failure can be complete or partial. A complete failure is characterized by transition of an object to a down state. A partial failure is characterized by transition of an object to partially down state.

13. Damage is an event that involves impairment of an object's operating condition while maintaining its up state (GOST 27.002-2015). A defect and/or damage may cause a partial or complete failure of an object. Present defect and/or damage render an object disabled.

14. Limiting state is a state of an object when its further operation is neither allowable nor feasible, or the recovery of its up state is neither possible nor feasible (GOST 27.002-2015).

15. Service life extension refers to activities aimed to prepare a NPP power unit for operation within the additional period (NP-017-2000).

16. Specialized organization is a legal entity engaged under a contract or civil contract to conduct design, engineering, materials science works on life characteristics management, having the conditions for performing the works, personnel trained in accordance with the established procedure to carry them out, and having a license from Rostechnadzor to carry out this type of work.

17. Technical state is the condition of an object characterized by a set of parameters set in the documentation that describe its ability to perform the required functions under the conditions in question (GOST 27.002-2015).

Technical diagnostics is the determination of technical state of an object (GOST 20911-89).

1. Objectives of technical diagnostics are as follows:

technical state monitoring;

searching for a location and determination of failure (malfunction) causes;

forecasting technical state.

2. The "technical diagnostics" term is used in the names and definitions of concepts when the tasks of technical diagnostics are equivalent or the main task is to find the place and determine the causes of failure (malfunction).

3. The "technical state monitoring" term is used when the main task of technical diagnostics is to determine the type of technical state.

18. Maintenance is a set of organizational measures and technical operations to maintain the operability (serviceability) of the object and reduce the probability of its failures when used for intended purpose, storage and transportation (GOST 27.002-2015). Main types of maintenance: scheduled maintenance is a maintenance carried out in accordance with the requirements of the documentation; unscheduled maintenance is a maintenance carried out without prior appointment, according to technical state.

19. Operating conditions refer to a combination of factors affecting the product during its operation (GOST 25866-83).

20. Test conditions is a set of influencing factors andor modes of operation of the object during testing (GOST 16504-81).

21. Electromagnetic compatibility is the ability of hardware to function with a given quality in a given electromagnetic environment and not to create unacceptable electromagnetic interference to other hardware (GOST R 50397-2011).

22. Electronic operational file of a product is a set of data that describes the physical structure of a product instance and characterizes events that occur with the product during operation, maintenance and repair (operating time, changes in the physical structure of the product instance, changes in the characteristics of the product and its components, failures and their elimination, etc.) (GOST R 53394-2017).

- Appendix 3 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

SUGGESTED LIST OF 
NPP I&C INCLUDED IN THE LIFE MANAGEMENT PROGRAM

1. Reactor plant instrumentation and control systems and equipment referred to safety class 2 according to NP-001-15:

initiating part of emergency protection (EP) and ESFAS;

actuating part of EP-WP related to emergency protection;

neutron flux monitoring system;

computerized subsystem of in-core instrumentation system related to emergency protection;

emergency coolant level monitoring system;

temperature monitoring equipment of the primary circuit.

2. Components of control and protection system - ESFAS related to safety class 2 according to NP-001-15:

1) connecting and switching equipment, including:

terminal boxes;

boards of intermediate terminal boxes;

cable studs in the containment;

2) low voltage switching devices;

3) primary and secondary metering transducers;

4) sensor test benches;

5) pulse pipelines;

6) monitoring and control cables.

3. Drives of CPS actuators.4

4. Electromagnets of PHRS air locks.

5. Pneumatic drives of isolating valves.

6. Components of I&C referred to safety class 3 according to NP-001-15 (installed by the operating organization).

- Appendix 4 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

A SUGGESTED LIST 
OF PARAMETERS THAT DETERMINE THE LIFE OF NPP I&C, FOR WHICH THE LIFE CHARACTERISTICS ARE SET

1. Electrical parameters of radio-electronic and microprocessor devices.

2. Physical and chemical properties of polymer insulation and sheath of cables and wires.

3. Electrical parameters of cables and wires.

4. State of windings (of electric machines, transformers).

5. The number of on-off cycles of  secondary circuit devices.

6. Resistance of contact elements of control equipment.

7. Strength and vibration resistance of equipment.

8. Time and time difference of closing and opening the relay contact elements and switches.

9. Other parameters not mentioned above.

- Appendix 5 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

A SUGGESTED LIST 
OF CRITERIA FOR THE EVALUATION OF PARAMETERS THAT DETERMINE THE LIFE OF NPP I&C

| Item | Parameters that determine the life of I&C | Evaluation criteria |
| --- | --- | --- |
| 1. | Electrical parameters of radio-electronic and microprocessor devices | Limit values established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, as well as established by the Specifications and/or technical requirements developed at the design and construction stage |
| 2. | Physical and chemical properties of polymer insulation and sheath of cables and wires | Limit value for insulation material set in national or industry standards included in the consolidated list of mandatory standardization documents in the field of atomic energy use |
| 3. | Electrical parameters of cables and wires | Limit values established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, as well as established by the Specifications and/or technical requirements developed at the design and construction stage |
| 4. | State of windings of electric machines, transformers | Limit value for windings (of electric motor, transformer) set in national or industry standards included in the consolidated list of mandatory standardization documents in the field of atomic energy use |
| 5. | The number of on-off cycles of secondary circuit devices | Limit values established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, as well as established by the Specifications and/or technical requirements developed at the design and construction stage |
| 6. | Resistance of contacts of control equipment |  |
| 7. | Strength and vibration resistance of equipment |  |
| 8. | Time and time difference of closing and opening the relay contact elements and switches |  |
| 9. | Other parameters not mentioned above |  |

- Appendix 6 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

RECOMMENDED 
MONITORING METHODS OF THE LIFE CHARACTERISTICS OF NPP I&C

| Item | Parameters that determine the life (controlled parameters) | Recommended monitoring methods (inspection and experimental test) |
| --- | --- | --- |
| 1. | Electrical parameters of radio-electronic and microprocessor devices | Methods established in the national standards included in the consolidated list of standardization documents in the field of atomic energy use, including: test of printed circuit board coatings; checking the characteristics of detachable connections; checking the parameters of inputs and outputs; checking the respons time; test for contact loss; accelerated tests. Examples. 1. Test methods for programmable controllers according to GOST R 51841-2001. 2. Methods of accelerated tests of samples and materials for the determination of residual life in accordance with GOST R 51372-99; GOST 9.707-81 |
| 2. | Physical and chemical properties of polymer insulation and sheath of cables and wires | Methods established in the national standards included in the consolidated list of standardization documents in the field of atomic energy use, including: analysis of the structure and composition of micro-samples of insulation materials by physical and chemical methods, including determination of stabilizers, antioxidants, plasticizers (Fourier-transform IR spectrometry, thermogravimetric analysis, differential scanning calorimetry); evaluation of the cable state based on frequency-dependent impedance and other electrical parameters; frequency-dielectric spectroscopy; measurement of the elastic modulus under compression of the polymer cable sheath; determination of the relative elongation at break. Examples. 1. Methods according to GOST 27905.2-88. Verification of aging mechanisms related to operation, physical and chemical methods on insulation systems, measurements related to aging factors, including: hardness measurements as per GOST 24621-2015; elasticity measurements as per GOST 24622-91; stiffness measurements as per GOST 25922-83; tension stress measurements as per GOST 11262-80; bend measurements as per GOST 4651-2014; elongation measurements as per GOST 11262-80; compression measurements as per GOST 4651-2014; impact measurements as per GOST 19109-84; visual inspection; chemical methods. 2. Methods of accelerated tests of I&C samples and their materials for the determination of residual life in accordance with GOST R 51372-99; GOST 9.707-81 |
| 3. | Electrical parameters of cables and wires | Methods established in the national standards included in the consolidated list of standardization documents in the field of atomic energy use, including: monitoring of dielectrical strength, including; the electric field strength value when dielectric material breaks down; insulation overvoltage testing; monitoring of insulation resistance, including: insulation resistance measurement; evaluation of the absorption characteristics of insulation (absorption coefficient, polarization index); reflectometry of electrical properties of cables, in particular: time domain reflectometry; partial discharge reflectometry; resonance frequency reflectometry; test of dielectric properties, including: measurement of frequency dielectric spectra (tangent of the dielectric loss angle); measurement of return voltage; measurement of isothermal relaxation current; measurement of leakage current and leakage current unbalance factor, including high rectified voltage test, with regard to rectified voltage ripples, if required. Examples. 1. General provisions on the organization and methodological support in accordance with GOST 27.905.1-88, 27.905.2-88, 27.905.3-88, 27.905.4-88. 2. Insulation resistance according to GOST 6433.2-71, GOST 10169-77 (ST SEV 1106-78, ST SEV 3559-82 (CMEA standards). 3. Permittivity as per GOST 6433.4-71. 4. Dielectric losses and their change depending on load and/or frequency according to GOST 6433.4-71. 5. Surface specific resistance according to GOST 6433.2-71. 6. Partial discharges, in particular: starting and attenuation voltage, amplitude, quantity, and other characteristics according to GOST 20074-83. 7. Dielectric properties as a function of temperature according to GOST 6433.2-71. 8. Verification test at DC and AC voltage as per GOST 6433.3-71 |
| 4. | State of windings (of electric machines, transformers) | Methods established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, including, inter alia, non-destructive test performed based on spectral analysis of the absorbed current and frequency dielectric spectroscopy. Example. Methods according to GOST 3484.1-88, GOST 3484.3-88, GOST 22756-77, GOST 10169-77 |
| 5. | The number of on-off cycles of secondary circuit devices | Methods established in the national standards included in the consolidated list of standardization documents in the field of atomic energy use. Recorded during operation by personnel based on observation data |
| 6. | Resistance of contacts of control equipment | Methods established in the national standards included in the consolidated list of standardization documents in the field of atomic energy use, including: measuring the transient resistance of contact elements; measurements of overtemperature of main and auxiliary circuits, contact groups at rated (maximum) load currents; measurement of voltage drop at the contact connection. Example. Requirements and methods according to provisions of GOST IEC 60947-5-4-2014 |
| 7. | Strength and vibration resistance of equipment | Methods established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, while equipment vibration is measured by vibration measuring equipment; strength is estimated by calculation, vibration resistance is to be confirmed by calculation (experimentally), and vibration resistance is to be confirmed experimentally. Examples. 1. GOST R ISO 17359-2015, which establishes recommendations for procedures used in the implementation of programs for state monitoring and diagnostics of machines (monitoring systems), including programs and methods for equipment state monitoring. 2. GOST ISO 10816-1-97; GOST ISO 7919-1-2002; that establish general guidelines for the measurement and evaluation of mechanical vibration of fixed and mobile machine elements, including: vibration displacement; vibration rate; vibration acceleration, and the procedure for setting their limit values. 3. GOST 32106-2013; assessment of the vibration state of hazardous production equipment during operation and acceptance tests after installation and repair |
| 8. | Time and time difference of closing and opening the main contact elements of switches | Methods established in national standards included in the consolidated list of standardization documents in the field of atomic energy use, including mechanical performance tests with measurement of time characteristics. Example. Test methods according to GOST R 52565-2006 provisions |
| 9. | Other parameters not mentioned above | Development of additional methods and their justification |

- Appendix 7 
to the safety guide in the use of atomic energy "Establishment and monitoring methods of the life characteristics of instrumentation and control devices of nuclear power plants" approved by  the Federal Environmental, Industrial and Nuclear Supervision Service order No. _______ 
dated ____ __________ 20__

LIST OF 
REFERENCES TO REGULATORY DOCUMENTS RECOMMENDED FOR USE IN THE MONITORING OF LIFE CHARACTERISTICS

| No. | Designation of document | Document name | Document details |
| --- | --- | --- | --- |
| 1 | GOST 10169-77 (ST SEV 1106-78, ST SEV 3559-82) | 3-phase synchronous machines. Test methods (with amendments Nos. 1-4) | Decree of the National Standards Committee of the Council of Ministers of the USSR dated January 28, 1977 No. 233 |
| 2 | GOST 11262-80 | Plastics. Tensile test method | Decree of the National Standards Committee of the USSR dated November 21, 1980 No. 5521 |
| 3 | GOST 16504-81 | The state system of testing products. Product test and quality inspection. General terms and definitions. | Decree of the National Standards Committee of the USSR dated December 8, 1981 No. 3425, enacted on January 1, 1982 |
| 4 | GOST 16962.2-90 | Electrical products. Test methods for resistance to external mechanic impacts | Decree of the State Committee of the USSR for the Products Quality Management and Standards dated May 23, 1990 No. 1266 |
| 5 | GOST 17359-2015 | State monitoring and diagnostics of machines. General guidelines. | Order of the Federal Agency for Technical Regulation and Metrology dated October 20, 2015 No. 1581-ст |
| 6 | GOST 17516.1-90 | Electrical products. General requirements in terms of resistance to external mechanic impacts | Decree of the State Committee of the USSR for the Products Quality Management and Standards dated May 23, 1990 No. 1265 Enacted by the Order of Rosstandart No. 1229-ст in the Russian Federation since January 1, 2013 |
| 7 | GOST 18311-80 | Electrical products. Terms and definitions of main concepts (with amendments No. 1, 2) | Decree of the National Standards Committee of the USSR dated December 30, 1980 No. 6180 |
| 8 | GOST 19109-84 | Plastics. Izod impact strength test | Valid from July 1, 1985 till July 01, 1990 according to the Decree of the State Standards Committee of the USSR No. 3197 dated September 12, 1984 <*> |
|  |  |  | <*> Restriction of the validity period is cancelled by the Minutes of the Interstate Council for Standardization, Metrology and Certification No. 4-93 (Reference Index No. 4, 1994). |
| 9 | GOST 20074-83 | Electrical equipment and installations. Measurement method of partial discharge parameters | Decree of the National Standards Committee of the USSR dated April 12, 1983 No. 1961 |
| 10 | GOST 22756-77 | Power and voltage transformers and reactors. Test methods of electric insulation strength | Decree of the National Standards Committee of the Council of Ministers of the USSR dated October 31, 1997 No. 2542 |
| 11 | GOST 23752.1-92 (IEC 326-2-90) | Printed boards. Test methods | Decree of the Committee for Standardization and Metrology of the USSR, dated January 30, 1992 No. 98 |
| 12 | GOST 24621-91 | Plastics and ebonite. Determination of indentation hardness by means of a durometer(Shore hardness) | Decree of the Committee for Standardization and Metrology of the USSR, dated December 29, 1991 No. 2328 This standard is prepared by direct application of the international standard ISO 868-85 Plastics and Ebonite. Determination of indentation hardness by means of a durometer (Shore hardness) with additional requirements that reflect the needs of the national economy |
| 13 | GOST 24622-91 | Plastics. Determination of hardness. Rockwell hardness | Decree of the Committee for Standardization and Metrology of the USSR, dated December 29, 1991 No. 2329 |
| 14 | GOST 25866-83 | Operation of technical equipment. Terms and definitions | Decree of the National Standards Committee of the USSR dated July 13, 1983 No. 3105 |
| 15 | GOST 25922-83 | Methods of hardness determination | Decree of the National Standard Committee of the USSR dated September 26, 1983 No. 4536 |
| 16 | GOST 27.002-2015 | Dependability of technical equipment. Fundamentals. Terms and definitions | Interstate Standard GOST 27.002-2015 was enacted as the national standard of the Russian Federation since March 1, 2017 by the Order of the Federal Agency for Technical Regulation and Metrology No. 654-ст dated June 21, 2016 |
| 17 | GOST 27597-88 | Electronics items. Corrosion resistance evaluation method | Decree of the National Standards Committee of the USSR dated February 26, 1988 No. 378 |
| 18 | GOST 27905.1-88 | Electrical insulation systems of electrical equipment. Evaluation and classification | International standard IEC 505-75 "Guide for the evaluation and identification of insulation systems of electrical equipment" was enacted directly as national standard of the USSR since January 01, 1990 by the Decree of the National Standards Committee of the USSR No. 3842 dated November 25, 1988. |
| 19 | GOST 27905.2-88 | Electrical insulation systems. Evaluation of performance, aging mechanism and diagnostic procedures | International standard IEC 791-84 Evaluation of insulation system performance based on operation experience and results of functional tests and Standard IEC 610-78 Key aspects for the functional evaluation of insulation systems of electrical equipment: aging mechanisms and diagnostics methods were enacted directly as a state standard of the USSR since January 1, 1990 by the Decree of the National Standards Committee of the USSR No. 3842 dated November 25, 1988 |
| 20 | GOST 27905.3-88 | Electrical insulation systems. Methods of multi-factor functional tests | Decree of the National Standards Committee of the USSR dated November 25, 1988 No. 3842 |
| 21 | GOST 27905.4-88 | Electrical insulation systems. Methods of electrical endurance evaluation | Decree of the National Standards Committee of the USSR dated November 25, 1988 No. 3842 |
| 22 | GOST 32106-2013 | State monitoring and diagnostics of machines. Hazardous equipment monitoring. Vibration generated by centrifugal and compressor units | Interstate standard GOST 32106-2013 was enacted as a national standard of the Russian Federation since November 1, 2014 by the Order of the Federal Agency for Technical Regulation and Metrology No. 1642-ст dated November 22, 2013 |
| 23 | GOST 3484.1-88 | Power transformers. Electromagnetic testing methods | Decree of the National Standards Committee of the USSR dated August 30, 1988 No. 3051 |
| 24 | GOST 3484.3-88 | Power transformers. Measuring methods of dielectric parameters of insulation | Decree of the National Standards Committee of the USSR dated August 30, 1988 No. 3051 |
| 25 | GOST 4651-2014 | Plastics. Compression test method | Interstate standard GOST 4651-2014 (ISO 604:2002) was enacted as a national standard of the Russian Federation since March 01, 2015 by the Order of the Federal Agency for Technical Regulation and Metrology No. 467-ст dated May 29, 2014 |
| 26 | GOST 50397-2011 | Electromagnetic compatibility for electronic equipment. Terms and definitions | Order of the Federal Agency for Technical Regulation and Metrology dated December 8, 2011 No. 756-ст |
| 27 | GOST R 51372-99 | Accelerated life and storable life test methods in aggressive and other special media for technical products, materials and systems of materials. General | Decree of Gosstandart of Russia dated November 29, 1999 No. 442-ст |
| 28 | GOST R 51841-2001 | Programmable controllers. General technical requirements and test methods | Decree of Gosstandart of Russia dated December 24, 2001 No. 556-ст |
| 29 | GOST R 52565-2006 | AC circuit breakers for voltages of 3 to 750 kV. General specifications | Order of the Federal Agency for Technical Regulation and Metrology dated August 23, 2006 No. 170-ст |
| 30 | GOST R 53394-2017 | Integrated logistic support. General terms and definitions. | Order of the Federal Agency for Technical Regulation and Metrology dated March 10, 2017 No. 109-ст |
| 31 | GOST 6433.2-71 | Solid electrical insulating materials. Methods for evaluation of electrical resistance at DC voltages | Decree of the National Standards Committee of the Council of Ministers of the USSR dated May 24, 1971 No. 1001 |
| 32 | GOST 6433.3-71 | Solid electrical insulating materials. Methods for evaluation of electrical resistance at AC (50 Hz) and DC voltage | Decree of the National Standards Committee of the Council of Ministers of the USSR dated May 24, 1971 No. 1002 |
| 33 | GOST 6433.4-71 | Solid electrical insulating materials. Methods for evaluation of dielectric power factor and permittivity at 50 Hz | Decree of the National Standards Committee of the Council of Ministers of the USSR dated May 24, 1971 No. 1003 |
| 34 | GOST 9.311-87 | Uniform corrosion and aging protection system (UCAPS). Metal and non-metal inorganic coatings. Method of corrosion damage evaluation (with amendment No. 1) | Decree of the National Standards Committee of the USSR dated February 17, 1986 No. 255 |
| 35 | GOST 9.707-81 | Uniform corrosion and aging protection system. Polymer materials. Methods of accelerated climatic ageing tests | Decree of the National Standards Committee of the USSR dated December 25, 1981 No. 5664 |
| 36 | GOST ISO 10816-1-97 | Vibration. Evaluation of machine vibration by measurements on non-rotating parts. Part 1. General requirements | Interstate standard GOST ISO 10816-1-97 was enacted immediately as a state standard of the Russian Federation since July 1, 1999 by the Decree of the State Committee of the Russian Federation for Standardization, Metrology and Certification No. 353 dated September 17, 1998 |
| 37 | GOST ISO 7919-1-2002 | Vibration. Evaluation of machine vibration by measurements on rotating shafts. General requirements | Interstate standard GOST ISO 7919-1-2002 was enacted as a national standard of the Russian Federation since November 1, 2007 by the Order of the Federal Agency for Technical Regulation and Metrology No. 76-ст dated April 24, 2007 |
| 38 | GOST IEC 60034-14-2014 | Rotating electrical machines. Part 14. Mechanical vibration of certain machines with shaft heights 56 mm and higher. Measurement, evaluation and limits of vibration | Order of the Federal Agency for Technical Regulation and Metrology dated May 25, 2015 No. 405-ст |
| 39 | GOST R IEC 61513-2011 | Nuclear Power Plants. Safety related instrumentation and control systems. General requirements | Order of the Federal Agency for Technical Regulation and Metrology dated September 28, 2011 No 377-ст. |
| 40 | GOST R IEC 62342-2016 | Nuclear Power Plants. Safety related monitoring and control. Ageing management | Order of the Federal Agency for Technical Regulation and Metrology dated June 09, 2016 No. 579-ст |
| 41 | GOST R IEC 62385-2012 | Nuclear Power Plants. Safety related monitoring and control. Assessment methods for the performance of safety system channels | Order of the Federal Agency for Technical Regulation and Metrology dated September 12, 2012 No. 291-ст |