- Approved by 
Order of the Federal Environmental, Industrial and Nuclear Supervision Service 
dated January 30, 2018 2018

SAFETY GUIDE 
IN THE USE OF ATOMIC ENERGY "EMERGENCY MONITORING SYSTEMS OF NUCLEAR POWER PLANTS WITH PRESSURIZED WATER REACTORS. GENERAL RECOMMENDATIONS AND THE RANGE OF CONTROLLED PARAMETERS"

(RB-140-17)

- I. General

1. This safety guide in the use of atomic energy "Emergency monitoring systems of nuclear power plants with pressurized water reactors. General recommendations and the range of controlled parameters" (RB-140-17) (hereinafter referred to as the Safety Guide) was developed in accordance with Article 6 of the Federal law dated November 21, 1995 No. 170-FZ "On the use of atomic energy" for compliance with the requirements of paragraph 3.1.5 of the Federal rules and regulations in the field of atomic energy use  "General provisions for NPP safety assurance" (NP-001-15), approved by the order of the Federal Environmental, Industrial and Nuclear Supervision Service No. 522 dated December 17, 2015 (registered by the Ministry of Justice of the Russian Federation on February 02, 2016 registration number No. 40939); requirements of paragraphs 45, 46, 47, 48, 49 of the Federal Rules and Regulations in the field of atomic energy use "Requirements for control systems related to NPP safety" (NP-026-16) approved by the Order of the Federal Environmental, Industrial and Nuclear Supervision Service No. 483 dated November 16, 2016 (registered by the Ministry of Justice of Russia on December 14, 2016, registration No. 44712), in terms of emergency monitoring of nuclear power plant parameters in the management of beyond-design basis accidents.

2. This Safety Guide contains general recommendations of the Federal Environmental, Industrial and Nuclear Supervision Service for emergency monitoring systems that are applicable to the design and operation of systems that perform emergency monitoring at nuclear power plants with pressurized water reactors, as well as in the safety analysis and assessment of design solutions selected. In addition, this Safety Guide contains recommendations on the range of controlled parameters of emergency monitoring required to assess the state of reactor plant, NPP power unit and nuclear power plant as a whole in the management of beyond-design basis accidents.

3. This Safety Guide is intended for use by NPP operating organizations and organizations performing any works and providing any services to the operating organizations in the course of development and design of emergency monitoring systems, as well as for use by the experts of Rostechnadzor in the course of their licensing (permitting) activities or federal state supervision in the field of atomic energy use.

4. The recommendations contained in this Safety Guide take into account the accumulated international experience in the development of emergency monitoring requirements for accident management, in particular, IAEA recommendations, as well as lessons learned from the experience of managing beyond design basis accidents.

5. The requirements of the Federal Rules and Regulations in the field of atomic energy use may be implemented through the use of any other techniques (methods) different from the ones specified in this Safety Guide subject to substantiation of the selected techniques (methods) for safety assurance.

6. The list of abbreviations used in these Safety Guides is given in Appendix 1, and the terms and definitions are given in Appendix 2.

- II. General recommendations for emergency monitoring

7. It is recommended to provide for emergency monitoring systems in the NPP design that are necessary for monitoring the state of RP and NPP under beyond-design basis, including severe, accidents. It is recommended that the scope of monitoring of RP and NPP state parameters established in the design should consider the recommendations of this Safety Guide and be sufficient to monitor the state of RP and NPP under BDBA conditions. It is recommended to develop instructions and guides that define the actions of personnel to manage BDBA with due regard to the design of emergency monitoring system for each specific power unit of the NPP.

8. It is recommended to display the parameters of RP and NPP monitored by the emergency monitoring system throughout the accident and in the post-accident period, until the NPP unit is transferred to a controlled safe state. It is recommended to justify the composition of parameters controlled at various stages of accidents in the NPP design and present in the NPP SAR. It is recommended to ensure that the controlled parameters are displayed on MCR, SCR, and EACPC.

9. It is recommended to provide emergency monitoring systems for all NPP power units under design, construction and operation. It is recommended to design an emergency monitoring system independent of the control normal operation systems and control safety systems.

10. It is recommended to set the range of controlled parameters of emergency monitoring in the RP and NPP design with due regard to design features for each power unit. It is recommended that the structure of special equipment for emergency monitoring and its characteristics, such as the range and accuracy of measurements, response speed, required duration of operation, resistance to external impacts, redundancy, reliability, independence and segregation, testability (controllability), protection against unauthorized access, maintenance and repair procedures should be justified and established in the design documentation of the NPP (hereinafter referred to as NPP design) and presented in the NPP SAR.

11. It is recommended to classify special equipment for emergency monitoring in accordance with the requirements of FRR and present in the NPP SAR.

12. When defining the scope of special equipment of emergency monitoring, it is recommended to consider the internal and external impacts that may complicate the receipt of information about the state of RP and NPP under BDBA, including emergency scenarios with prolonged loss of power, loss of contact with MCR or РГГУ, interrupted contact with external infrastructure, loss of resistance to external impacts.

13. When defining the range of controlled parameters of emergency monitoring for a multi-unit NPP, it is recommended to take into account the possibility of a beyond-design basis, including severe, accident simultaneously at all units of the NPP.

14. It is recommended to choose special equipment for emergency monitoring with due regard to environmental conditions during accidents (for example, seismic effects, air shock waves, ionizing radiation, temperature, humidity).

15. It is recommended to provide means of protection of special equipment of emergency monitoring system, including software, against unauthorized interference.

16. It is allowed to use special equipment of the emergency monitoring system as an indicator of the presence or absence of a physical quantity. It is allowed to use measuring channels of control systems of normal operation and control safety systems as special equipment of emergency monitoring. It is recommended to justify the use of control systems of normal operation and control safety systems as special equipment of emergency monitoring in the NPP design and present in the NPP SAR.

17. It is recommended to provide for a self-diagnosis function for special equipment of emergency monitoring.

18. It is recommended to supply power to special equipment of emergency monitoring so that it can retain the up state within a reasonable time justified in the NPP design in case of failure of power supply sources for normal operation and emergency power sources of the second group of the emergency power system.

19. It is recommended to provide emergency monitoring for each of the controlled parameters by several channels, ensuring, if possible, their compliance with the independence principle. Information from the emergency monitoring system shall be recorded and stored in autonomous registration and information storage facilities.

20. When defining the range of controlled parameters, it is recommended to take into account all locations of nuclear fuel at the NPP, such as reactor, spent fuel pool, nuclear fuel storage facilities, as well as places where nuclear fuel is located during transportation (FA and SFA).

21. It is recommended to take into account the mutual relationship between the BDBA manual and the scope of parameters of the emergency monitoring system, namely:

the BDBA manual is developed in accordance with the current state of NPP (NPP power unit) in terms of the scope and characteristics of emergency monitoring equipment;

a simultaneous change in the design of emergency monitoring system may be required to implement a new BDBA manual at the existing NPP (NPP power unit).

- III. Recommendations for the range of emergency monitoring parameters

22. When establishing the range of parameters and characteristics of special equipment for emergency monitoring, it is recommended to proceed from the fact that emergency monitoring should provide the personnel responsible for managing BDBA with the necessary information:

a) to determine the status of main safety functions,

such as

emergency shutdown of the reactor and its maintenance in the subcritical state;

emergency heat removal from the reactor (heat removal from the reactor core and from fuel elements located in storage facilities and other places);

retaining radioactive substances within the specified limits and keeping radioactive substances from the discharge into the environment (inter alia, ensuring the integrity of the containment);

b) to perform actions provided for by BDBA manual.

23. It is recommended to determine the range of parameters with due regard to the need to identify the controlled parameters required for:

obtaining information about a potential threat or actual loss of integrity of physical barriers in the way of discharge of radioactive substances;

obtaining information about the status of safety systems and equipment for BDBA management;

evaluation of the amount of radioactive substances released.

24. A suggested list of emergency monitoring parameters is given in Appendix 3 to this Safety Guide.

It is recommended that the final list of emergency monitoring parameters should be justified and established in the NPP design and presented in the NPP SAR.

25. It is recommended to determine the minimum necessary set of equipment within special equipment for emergency monitoring that will remain in the up state, if a BDBA progresses to a severe stage. A full list of monitoring parameters in a severe accident shall be developed in the NPP design in accordance with the severe accident management strategy. For a severe BDBA, it is recommended to provide emergency monitoring of at least the following parameters:

temperature at FA outlet;

pressure in reactor vessel;

temperature of the reactor vessel head;

coolant level and temperature in the fuel pool;

medium pressure, humidity and temperature in the atmosphere inside the containment;

composition of explosive mixtures (hydrogen, carbon monoxide) in the atmosphere inside the containment;

gamma radiation dose rate inside the containment.

It is recommended to provide monitoring of parameters that characterize the state of CC for RPs with VVER equipped with a corium catcher.

26. It is recommended to use special equipment of emergency and post-accident sampling system, including means of emergency sampling from reactor coolant, fuel pool and steam-gas medium from the atmosphere below the containment under accident conditions to obtain more information about the state of RP and NPP as a whole to assess the potential threat of environmental pollution under BDBA. Sampling provides prompt determination of the activity of radionuclides present in the sample, as well as monitoring of the following indicators:

concentrations of hydrogen and oxygen in spaces inside the containment;

boric acid concentrations in the coolant, fuel pool and refueling pool, and ECCS tanks;

pH of water accumulating at the lower levels of sealed spaces of the RP (water tanks and emergency sump tanks);

concentrations of radionuclides of iodine, radioactive noble gases and aerosols inside the containment.

- Appendix 1 
to the safety guide in the use of atomic energy "Emergency monitoring systems of nuclear power plants with pressurized water reactors. General recommendations and the range of controlled parameters" approved by the Order of the Federal Environmental, Industrial and Nuclear Supervision Service 
No. 42 dated January 30, 2018

ABBREVIATIONS

| NPP | - | Nuclear Power Plant |
| --- | --- | --- |
| MCR | - | main control room |
| VVER | - | pressurized water reactor |
| - | - | containment |
| BDBA | - | beyond design basis accident |
| PERCP | - | protected emergency response control post |
| SG | - | steam generator |
| ECR | - | Emergency Control Room |
| RF | - | Reactor Facility |
| BDBA manual | - | Beyond Design Basis Accident management manual |
| ECCS | - | emergency core cooling system |
| PHRS | - | passive heat removal system |
| FA | - | Fuel Assembly |
| FE | - | Fuel Element |
| NPP SAR | - | Nuclear Power Plant Safety Analysis Report |
| SFA | - | Spent Fuel Assembly |
| CC | - | Corium Catcher |
| FRR | - | Federal Rules and Regulations in the field of atomic energy use |

- Appendix 2 
to the safety guide in the use of atomic energy "Emergency monitoring systems of nuclear power plants with pressurized water reactors. General recommendations and the range of controlled parameters" approved by the Order of the Federal Environmental, Industrial and Nuclear Supervision Service 
No. 42 dated January 30, 2018

TERMS AND DEFINITIONS

The following terms and definitions are used in this Safety Guide.

Controlled safe state of the nuclear power plant refers to the NPP state maintained within an infinite period when all basic NPP safety functions specified in General Safety Provisions for Nuclear Power Plants are ensured.

Monitoring is the collection, display, registration, storage and analysis of parameters of RP and NPP that directly or indirectly characterize the state of safety of RP and NPP.

Emergency monitoring system is a set of special equipment designed to monitor the state of RP and NPP in case of BDBA.

Special-purpose hardware for beyond design basis accident management refers to control systems (components) provided in the NPP design for the management of beyond design basis accidents.

Severe accident is a BDBA with fuel element damage above the design limit.

- Appendix 3 
to the safety guide in the use of atomic energy "Emergency monitoring systems of nuclear power plants with pressurized water reactors. General recommendations and the range of controlled parameters" approved by the Order of the Federal Environmental, Industrial and Nuclear Supervision Service 
No. 42 dated January 30, 2018

SUGGESTED LIST OF EMERGENCY MONITORING PARAMETERS <1>

--------------------------------

<1> The list of emergency monitoring parameters is established in the design of RP and NPP taking into account the specifics of each power unit and specific lists of BDBA scenarios.

1. Neutron flux power level and reactor period.

2. Coolant temperature at FA outlet.

3. Water level in reactor.

4. Coolant temperature in "hot" legs of  reactor coolant pipeline loops.

5. Pressure in the reactor vessel (above the core).

6. Water level in the pressurizer.

7. Temperature of the reactor vessel head.

8. Boric acid concentration in primary coolant.

9. Boiler water levels in steam generators.

10. Steam pressure in steam pipelines of steam generators.

11. Water level in the fuel pool.

12. Water temperature in the fuel pool.

13. Primary coolant activity.

14. Activity and concentration of boric acid in fuel pool water.

15. Water level in the containment sump (sump tank).

16. Level of boric acid solution in ECCS hydroaccumulators, hydroaccumulators of the second (third) stage.

17. Pressure in ECCS hydroaccumulators, hydroaccumulators of the second (third) stage.

18. Levels of boriv acid solution in ECCS tanks.

13. Dose rate inside the containment.

20. Pressure inside the containment.

21. Flow rate of sprinkler system solution.

22. Hydrogen concentration inside the containment.

23. Concentration of oxygen and water vapor inside the containment.

24. Atmosphere temperature inside the containment.

25. Water level in the CC shaft.

26. Water levels in tanks used for the supply of emergency feed water to steam generators.

27. Water level in PHRS tanks <2> (for PHRS using water).

--------------------------------

<2> The list of emergency monitoring parameters is compiled for existing and newly designed NPPs. It should be noted that not all parameters of newly designed NPPs are applicable for existing NPPs.

28. Flow rate of essential service water.

29. Flow rate in the systems of intermediate circuits related to safety systems.

30. Radiation parameters (dose rate inside the containment, in the annex of reactor building, etc.).